RURAL ELECTRIFICATION AGENCY

BID FORM 1: TECHNICAL DATA SHEETS

|  | MATERIAL/EQUIPMENT | UNIT | REQUIRED | BIDDER’S MANUFACTURER SPECIFICATIONS | COMPLIANCE |
| --- | --- | --- | --- | --- | --- |
| 1 | Pole Mounted 3 phase Distribution Transformers 33/0.415/0.22kV, 25kVA |  |  |  |  |
| A | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| B | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 33 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 25 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 36 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.15 |  |  |
|  | Load Losses | kW | 0.48 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 45 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A | 0.45 |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 70 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 170 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 3 |  |  |
|  | Minimum base thickness | mm | 3 |  |  |
|  | Minimum Cover plate thickness | mm | 4 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 294 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 294 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 900 |  |  |
|  | Assessment |  |  |  |  |
| 2 | Pole Mounted 3 Phase Distribution Transformers 33/0.415/0.22kV, 50kVA |  |  |  |  |
| a | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| b | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 33 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 50 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 36 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.25 |  |  |
|  | Load Losses | kW | 0.68 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 48 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A | 0.87 |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 70 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 170 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 3 |  |  |
|  | Minimum base thickness | mm | 3 |  |  |
|  | Minimum Cover plate thickness | mm | 4 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 294 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 294 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 900 |  |  |
|  | Assessment |  |  |  |  |
| 3 | Pole Mounted 3 Phase Distribution Transformers, 33/0.415/0.22kV, 100kVA |  |  |  |  |
| a | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| b | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 33 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 100 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 36 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.43 |  |  |
|  | Load Losses | kW | 1.25 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 50 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A | 1.74 |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 70 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 170 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 3 |  |  |
|  | Minimum base thickness | mm | 3 |  |  |
|  | Minimum Cover plate thickness | mm | 4 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 294 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 294 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 900 |  |  |
|  | Assessment |  |  |  |  |
| 4 | Pole Mounted 3 Phase Distribution Transformers, 33/0.415/0.22kV, 200kVA |  |  |  |  |
| a | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| b | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 33 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 200 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 36 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.63 |  |  |
|  | Load Losses | kW | 2.5 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 51 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A | 3.48 |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 70 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 170 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 3 |  |  |
|  | Minimum base thickness | mm | 3 |  |  |
|  | Minimum Cover plate thickness | mm | 4 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 294 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 294 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 900 |  |  |
|  | Assessment |  |  |  |  |
| 5 | Pole Mounted 3 Phase Distribution Transformers, 33/0.415/0.22kV, 315kVA |  |  |  |  |
| a | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| b | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 33 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 315 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 36 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.8 |  |  |
|  | Load Losses | kW | 3.5 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 51 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A |  |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 70 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 170 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 3 |  |  |
|  | Minimum base thickness | mm | 3 |  |  |
|  | Minimum Cover plate thickness | mm | 4 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 294 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 294 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 900 |  |  |
|  | Assessment |  |  |  |  |
| 6 | Pole Mounted 3 Phase Distribution Transformers, 33/0.415/0.22kV, 500kVA |  |  |  |  |
| a | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| b | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 33 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 500 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 36 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Ground on a plinth, surrounded with metal cage |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 1.0 |  |  |
|  | Load Losses | kW | 4.25 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 56 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A |  |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 70 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 170 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 6 |  |  |
|  | Minimum base thickness | mm | 6 |  |  |
|  | Minimum Cover plate thickness | mm | 6 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 294 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 294 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 900 |  |  |
|  | Assessment |  |  |  |  |
| 7 | 25kVA, 11/0.433 kV TRANSFORMERS |  |  |  |  |
| A | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| B | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 11 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 25 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 12 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.15 |  |  |
|  | Load Losses | kW | 0.605 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 45 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A |  |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 28 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 75 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 3 |  |  |
|  | Minimum base thickness | mm | 3 |  |  |
|  | Minimum Cover plate thickness | mm | 4 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 116 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 116 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 300 |  |  |
|  | Assessment |  |  |  |  |
| 8 | 50kVA, 11/0.433 kV TRANSFORMERS |  |  |  |  |
| a | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| b | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 11 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 50 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 12 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.175 |  |  |
|  | Load Losses | kW | 1.305 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 48 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A |  |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 28 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 75 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 3 |  |  |
|  | Minimum base thickness | mm | 3 |  |  |
|  | Minimum Cover plate thickness | mm | 4 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 116 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 116 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 300 |  |  |
|  | Assessment |  |  |  |  |
| 9 | 100kVA, 11/0.433 kV TRANSFORMERS |  |  |  |  |
| a | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| b | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 11 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 100 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 12 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.325 |  |  |
|  | Load Losses | kW | 2.135 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 50 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A |  |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 28 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 75 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 3 |  |  |
|  | Minimum base thickness | mm | 3 |  |  |
|  | Minimum Cover plate thickness | mm | 4 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 116 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 116 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 300 |  |  |
|  | Assessment |  |  |  |  |
| 10 | 200kVA, 11/0.433 kV TRANSFORMERS |  |  |  |  |
| a | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| b | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 11 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 200 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 12 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.4 |  |  |
|  | Load Losses | kW | 2.850 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 51 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A |  |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 28 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 75 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 3 |  |  |
|  | Minimum base thickness | mm | 3 |  |  |
|  | Minimum Cover plate thickness | mm | 4 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 116 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 116 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 300 |  |  |
|  | Assessment |  |  |  |  |
| 11 | 315kVA, 11/0.433 kV TRANSFORMERS |  |  |  |  |
| a | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| b | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 11 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 315 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 12 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.51 |  |  |
|  | Load Losses | kW | 3.850 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 55 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A |  |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 28 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 75 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 3 |  |  |
|  | Minimum base thickness | mm | 3 |  |  |
|  | Minimum Cover plate thickness | mm | 4 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 116 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 116 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 300 |  |  |
|  | Assessment |  |  |  |  |
| 12 | 500kVA, 11/0.433 kV TRANSFORMERS |  |  |  |  |
| a | Manufacturer Assessment |  |  |  |  |
|  | Name |  | Name of Supplier |  |  |
|  | Provide detail of legal status of the company |  | Copy of Company Registration certificate |  |  |
|  | Provide details of the premises |  | Copy of Business trading licence |  |  |
|  | Years of existence |  | Proof of existence for the past 10 years |  |  |
|  | Reference list of similar supply contracts |  | Detailed list of clients with full contacts addresses |  |  |
|  | Quality Management System |  | Copy of ISO 9001:2008 certificate or equivalent |  |  |
|  | Product type test reports by an internationally recognised electrical testing laboratory |  | Copy of Reports. Those issued beyond 3 years should be certified by issuer. |  |  |
|  | Routine test reports for each product |  | Copies of recent reports should |  |  |
|  | Manufacturer’s authorization letter. |  | Original copy, dully signed and sealed |  |  |
|  | Manufacturer’s guaranteed technical specifications |  | Original copy, dully signed and sealed and supported the respective authorization letter |  |  |
| b | Product Technical Assessment |  |  |  |  |
|  | Warranty | Years | 2 |  |  |
|  | Standard |  | IEC 60076-1-2-3-4-5-10 or equivalent |  |  |
|  | Rated High Voltage | kV | 11 |  |  |
|  | Rated Low Voltage | kV | 0.433 |  |  |
|  | Rated Power | kVA | 500 |  |  |
|  | Service Altitude | m | 1500 |  |  |
|  | Minimum Service Life | Years | 20 |  |  |
|  | Rated Highest System Voltage | kV | 12 |  |  |
|  | Insulation Class |  | A |  |  |
|  | Mounting |  | Pole |  |  |
|  | Number of Phases |  | 3 |  |  |
|  | Frequency | Hz | 50 |  |  |
|  | Vector Group |  | Dyn11 |  |  |
|  | Number of Windings |  | 2 |  |  |
|  | Type of winding |  | Copper wire or foil |  |  |
|  | No Load losses | kW | 0.710 |  |  |
|  | Load Losses | kW | 4.850 |  |  |
|  | Maximum Ambient Temperature | 0c | 40 |  |  |
|  | Cooling Method |  | ONAN |  |  |
|  | Noise level at measuring distance of 2m in accordance to IEC 551 | dB (A) | 56 |  |  |
|  | Type of Core |  | Three Limbs Stacked |  |  |
|  | Core Material |  | Cold Rolled Grain Oriented Silicon Steel |  |  |
|  | Core Cutting Technology |  | Step-Lap Technology |  |  |
|  | Impedance at rated power and voltage | % | 4 |  |  |
|  | Tapping Range (off Load) | +/-% | 0,2.5,5 |  |  |
|  | Number of steps | No. | 5 |  |  |
|  | Rated Current tap changer | A |  |  |  |
|  | Power Frequency Withstand Voltage of HV winding | kVrms | 28 |  |  |
|  | Power Frequency Withstand Voltage of LV winding | kVrms | 3 |  |  |
|  | HV Break Down insulation Level (BIL) | kVpeak | 75 |  |  |
|  | LV Break Down insulation Level (BIL) | kVpeak | 6 |  |  |
|  | Over Load Capacity | % | 20 |  |  |
|  | Temperature Rise Windings Top Oil | oC oC | 60 55 |  |  |
|  | Type of Tank |  | Hermetically sealed |  |  |
|  | Tank Protective Coating Type |  | Hot Dip Galvanised & Powder Coated |  |  |
|  | Tank Protective Coating thickness | um | 100 |  |  |
|  | Minimum Tank Thickness | Mm | 6 |  |  |
|  | Minimum base thickness | mm | 6 |  |  |
|  | Minimum Cover plate thickness | mm | 6 |  |  |
|  | Minimum Flange thickness | mm | 6 |  |  |
|  | Minimum Radiator thickness | mm | 1.2 |  |  |
|  | Insulating Medium Type |  | Mineral Oil |  |  |
|  | Insulating Medium Breakdown Voltage | kV | 70 |  |  |
|  | Insulating Medium method of filling |  | Vacuum |  |  |
|  | Clearances |  |  |  |  |
|  | Minimum HV Phase to Phase | mm | 116 or As per IEC 60076-3 |  |  |
|  | Minimum HV Phase to Earth | mm | 116 or As per IEC 60076-3 |  |  |
|  | Insulator Creepage distance min (25mm/kV) | mm | 300 |  |  |
|  | Assessment |  |  |  |  |